Carbon Emission (kgCO2e) = Charge x Emission Factor

In Scope1, the fugitive emission should be covered, for the refrigerant emission, the factor of the formula is set as:

Fugitive Carbon Emission of Refrigerant (kgCO2e) = C x L x GWP

C (Capacity): The total amount of refrigerant inside the AC unit (in kg), can be calculated by (Cooling Capacity x Charge Factor)

*Charge Factor can be defined by the rule of thumb, an engineering rule

L (Leakage): The percentage of gas that leaks per year (The Intergovernmental Panel on Climate Change IPCC stated, assuming 5%)

GWP (Global Warning Potential) : Value depends on specific gas type, can get from IPCC

From the research from the U.S EIA (Energy Information Administration),the reduced carbon emissions = energy savings (measured in kWh).

In Scope2, the indirect emissions of purchased energy should be covered, the formula is set as:

Indirect Emission of Purchased Energy(kgCO2e)= Electricity Usage x GEF

GEF(Grid Emission Factor): Determine according to the geographical location. In Hong Kong, the GEF is determined as 0.38 (CLP) and 0.6 (HKElectric). The unit is (kgCO2/kWh).

Enthalpy (in kJ/kg) = 1.006T + W(2501+1.86T)

T: Temperature (°C )

W: Humidity ratio (Water ratio to dry air)

1.006 = Specific heat of dry air

2501 = latent heat of vaporisation

1.86 = specific heat of water vapor

2. Calculate the Cooling Load

Qtotal = p x V x (Enthalpy outdoor - Enthalpy indoor)

Qtotal: The total heat removed by the air-conditioner, in kJ

p: Air Density, 1.2kg/m3

V: Volume of the room

Enthalpy: Calculated in step 1

3. Calculate the Cooling Power

Cooling Power = Qtotal/t

Cooling Power: in kW

Qtotal: Calculated in step 2

t: Time, 3600 seconds in 1 hour

4. Calculate Electricity Consumption

EkWh= (Cooling Power x Operating Time)/ COP

EkWh: Electricity consumed, in kWh

Cooling Power: Calculated in step 3

Operating Time: in hours

Coefficient of Performance (COP) : Air-conditioner’s efficiency, usually in range from 2.5 - 4.0 for modern Air-con unit

2.2.2 Calculation of lighting electricity consumption:

During the calculation, there are several points (marked with *) need to be considered.

- Calculate the illuminance of the light bulb generated

Eelec = Etotal - Edaylight

*The daylight should be considered and do further data adjustment before the calculation of energy. The sensor measures Total Illuminance (Etotal). The Electric Illuminance (Eelec) should be isolated.

*The daylight illuminance can be measured in a certain specific time when the room turns off all lights.

- Calculate Total Lumens (lm)

lm = (Eelec x Area)/CU x LLF

*Not all light from the bulb reaches the light sensors. Much of it hits the walls or ceiling. Therefore, the coefficient of utilisation(CU) should be applied in the calculation. In a typical room,the CU is often around 0.5 to 0.7.

*Some accounts for dust on the bulbs and the fact that LEDs dim slightly as they get older. The light loss factor (LLF) usually assumed to be 0.85 can be applied. (from Illuminating Engineering Society Recommended Practices -7)

- Determine Electrical Power

Electric Power = lm/Luminous Efficacy

lm: Calculated in step 2

*Modern LED lighting systems generally exhibit luminous efficacies around 100–120 lm/W, which is consistent with experimental studies reporting average values of approximately 105 lm/W for commercial LED lamps (Kurek, 2024).

- Calculate the energy consumption

EkWh = (Power x Hours of usage)/1000

EEI = (EC/Area) x (Obase/Oactual)

EC: Total Energy Consumption calculated

Area: Room Area

Obase: From ASHRAE Standard, computer teaching laboratory’s base occupancy suggested 0.1 person/m2

Oactual: Actual occupancy in the room

Fugitive Carbon Emission of Refrigerant (kgCO2e) = C x L x GWP

*No refrigerant information can be found in CityU BIM lab, therefore type R-410A (old standard) and 5kW cooling capacity air-con is assumed

For R-410A:

GWP:2285 (From IPCC AR6)

Charge Factor: 0.35kg/kW (By Rule of Thumb)

3.3.2 Scope2

Scope2: Indirect Emissions,covers emissions from the generation of purchased energy, mostly the electricity.

3.3.2(a) Air-Conditioner Energy Consumption

By combining the calculation procedure in 2.2.1

The energy consumption for an hour (EkWh)

EkWh= (p x V x ΔΔEnthalpy)/(3600 x COP)

*750ft2=69.677m2≈70m2

Volume of the room ≈ 70m2 x 3m =210m3

COP: Assumed as 3

Eelec = Etotal - Edaylight

*Before the energy calculation, the average value of the sensors are suggested to be use

lm = (Eelec x Area)/CU x LLF

*The  coefficient of utilisation(CU) should be applied in the calculation. In a typical room,the CU is often around 0.5 to 0.7.

*The light loss factor (LLF) usually assumed to be 0.85

Electric Power = lm/Luminous Efficacy

* Luminous Efficacy assumed 105 lm/W

EkWh = (Power x Hours of usage)/1000

Indirect Emission of Purchased Energy(kgCO2e)= Electricity Usage x GEF

Electricity : Summation of the results from 3.3.2 (a),(b),(c),in kWh

GEF: The City University of Hong Kong is located in Kowloon, therefore CLP’s index (0.38) is applied.

3.4 Energy Efficiency Assessment

EEI = (EC/Area) x (Obase/Oactual)